## heatSystemData
Heating system data table | Default Heating System Efficiencies |  |  |  | efficiency = polynomial function of HWRT or OAT
SystemType | DefaultDistribEff | DefaultControlskW | DefaultHeatingEff | EffUnits | FourthOrderPower | ThirdOrderPower | SecondOrderPower | FirstOrderPower | Constant | CurveEffUnits | OATcutout | OAThi | HWSTlo | OATlo | HWSThi | SysDT | Notes
condGasBoilerOAreset | 0.97 | 0.02 | 0.95 | ThermalEfficiency | -1.6528e-08 | 2.2123e-06 | -7.1901e-05 | 0.00064409 | 0.89292 | ThermalEfficiency |  | 60 | 120 | 10 | 170 | 15 | thermal efficiency as function of HWRT
condGasBoilerNoOAreset | 0.95 | 0.02 | 0.95 | ThermalEfficiency | 0 | 0 | 0 | 0 | 0.8934 | ThermalEfficiency |  | 60 | 170 | 10 | 170 | 15 | thermal efficiency as function of HWRT
nonCondGasOrOilBoilerOAreset | 0.97 | 0.02 | 0.84 | ThermalEfficiency | 0 | 0 | 0 | 0.00011581 | 0.83331 | ThermalEfficiency |  | 60 | 140 | 10 | 170 | 15 | thermal efficiency as function of HWRT
nonCondGasOrOilBoilerNoOAreset | 0.95 | 0.02 | 0.84 | ThermalEfficiency | 0 | 0 | 0 | 0 | 0.83375 | ThermalEfficiency |  | 60 | 170 | 10 | 170 | 15 | thermal efficiency as function of HWRT
condGasFurnace | 0.925 | 0.02 | 0.92 | AFUE | 0 | 0 | 0 | 0 | 0.92 | AFUE
nonCondGasOrOilFurnace | 0.925 | 0.02 | 0.8 | AFUE | 0 | 0 | 0 | 0 | 0.8 | AFUE
electricResistance | 1 | 0 | 0.99 | ThermalEfficiency | 0 | 0 | 0 | 0 | 0.99 | ThermalEfficiency
ASHPlessThan6TonsDucted | 0.92 | 0.02 | 3.05 | ASHP_COP47F | 0 | -2.2722e-06 | 0.00054546 | -0.0097198 | 2.5378 | COP | [6 empty] | COP curve as function of OAT drybulb. User entered heating efficiency as COP at 47F can be used to adjust the constant, shifting the curve up or down.
ASHPlessThan6TonsNonDucted | 0.96 | 0.02 | 3.05 | ASHP_COP47F | 0 | -2.2722e-06 | 0.00054546 | -0.0097198 | 2.5378 | COP | [6 empty] | COP curve as function of OAT drybulb
ASHPorVRFgreaterThan6TonsDucted | 0.92 | 0.02 | 3.25 | ASHP_COP47F | 0 | 1.3571e-05 | -0.00021865 | 0.01921 | 1.4211 | COP | [6 empty] | COP curve as function of OAT wetbulb
ASHPorVRFgreaterThan6TonsNonDucted | 0.96 | 0.02 | 3.5 | ASHP_COP47F | 0 | 1.3571e-05 | -0.00021865 | 0.01921 | 1.6711 | COP | [6 empty] | COP curve as function of OAT wetbulb
PTACorPTHP | 1 | 0.02 | 3.5 | ASHP_COP47F | 0 | 0 | -0.00064172 | 0.074939 | 1.3955 | COP | 35 | [5 empty] | linear fit is only good down to 40F. Below that COP is 1 for resistance heat. Adjust constant using user entered COP47 if different from default value.
waterSourceHeatPump | 0.96 | 0.03 | 5 | averageCOP | 0 | 0 | 0 | 0 | 5 | COP
groundSourceHeatPump | 0.96 | 0.03 | 3.5 | averageCOP | 0 | 0 | 0 | 0 | 3.5 | COP
air2WaterHeatPump | 0.97 | 0.02 | 3 | ASHP_COP47F | 0 | 0 | 0 | 0 | 3 | COP
none
heating efficiency units dropdown list
combined heating/cooling drop down list | description | [5 empty] | OAT for rated efficiency
condGasBoilerOAreset | condensing gas boiler with outdoor air reset |  |  |  |  | ThermalEfficiency | 50
condGasBoilerNoOAreset | condensing gas boiler no outdoor air reset |  |  |  |  | AFUE | NA
nonCondGasOrOilBoilerOAreset | non-condensing gas/oil boiler with outdoor air reset |  |  |  |  | ASHP_COP47F | 47
nonCondGasOrOilBoilerNoOAreset | non-condensing gas/oil boiler no outdoor air reset |  |  |  |  | ASHP_HSPF | 17
condGasFurnace | condensing gas furnace |  |  |  |  | averageCOP | 5
nonCondGasOrOilFurnace | non-condensing gas/oil furnace |  |  |  |  | NA | NA
ASHPlessThan6TonsDucted | air source heat pump < 6 tons - ducted
ASHPlessThan6TonsNonDucted | air source heat pump < 6 tons - non-ducted
ASHPorVRFgreaterThan6TonsDucted | air source heat pump or VRF >= 6 tons ducted
ASHPorVRFgreaterThan6TonsNonDucted | air source heat pump or VRF >=6 tons non-ducted
electricResistance | electric resistance
PTACorPTHP | packaged terminal air conditioner or heat pump
waterSourceHeatPump | water source heat pump |  |  |  |  | cooling efficiency units dropdown list
groundSourceHeatPump | ground source heat pump
air2WaterHeatPump | air to water heat pump |  |  |  |  | CoolingEER | 95
windowAirConditioner | window air conditioner |  |  |  |  | CoolingEER2 | 95
waterCooledChiller | water cooled chiller |  |  |  |  | CoolingSEER | NA
airCooledChiller | air cooled chiller |  |  |  |  | CoolingSEER2 | NA
none | none |  |  |  |  | CoolingIEER | NA
[6 empty] | CoolingIPLV | NA
[6 empty] | WSHP_COPaverage | NA
[6 empty] | GSHP_COPaverage | NA
[6 empty] | CoolingCOP | 95
NA