## heatSystemData
Cooling system data table | Default Cooling System Efficiencies |  |  |  | efficiency = polynomial function of outdoor air temp °F
SystemType | defaultDistribEff | defaultControlskW | defaultCoolingEff | effUnits | x4thPower | x3rdPower | x2ndPower | x1stPower | constant | curveEffUnits
windowAirConditioner | 1 | 0.01 | 2.9 | averageCOP | 0 | 0 | 0 | 0 | 2.9 | COP | COP curve as function of OAT drybulb
ASHPlessThan6TonsDucted | 0.92 | 0.02 | 2.9 | ASHP_COP95F | 0 | 2.6397e-06 | -0.00027678 | -0.057172 | 8.5661 | COP
ASHPlessThan6TonsNonDucted | 0.96 | 0.02 | 2.9 | ASHP_COP95F | 0 | 2.6397e-06 | -0.00027678 | -0.057172 | 8.5661 | COP
ASHPorVRFgreaterThan6TonsDucted | 0.92 | 0.02 | 3.1 | ASHP_COP95F | 0 | 2.6541e-06 | -0.00074346 | 0.023959 | 5.2581 | COP
ASHPorVRFgreaterThan6TonsNonDucted | 0.96 | 0.02 | 3.1 | ASHP_COP95F | 0 | 2.6541e-06 | -0.00074346 | 0.023959 | 5.2581 | COP
PTACorPTHP | 1 | 0.02 | 2.9 | ASHP_COP95F | 0 | 0 | 0 | -0.040761 | 6.7723 | COP
waterSourceHeatPump | 0.97 | 0.03 | 4.395 | averageCOP | 0 | 0 | 0 | 0 | 4.395 | COP
groundSourceHeatPump | 0.97 | 0.03 | 6.1529 | averageCOP | 0 | 0 | 0 | 0 | 6.1529 | COP
air2WaterHeatPump | 0.97 | 0.02 | 2.9 | averageCOP | 0 | 0 | 0 | 0 | 2.9 | COP
waterCooledChiller | 0.97 | 0.05 | 5.5 | averageCOP | 0 | 0 | 0 | 0 | 5.5 | COP
airCooledChiller | 0.97 | 0.05 | 3.7 | averageCOP | 0 | 0 | 0 | 0 | 3.7 | COP
none
combined heating/cooling drop down list | description
condGasBoilerOAreset | condensing gas boiler with outdoor air reset
condGasBoilerNoOAreset | condensing gas boiler no outdoor air reset
nonCondGasOrOilBoilerOAreset | non-condensing gas/oil boiler with outdoor air reset
nonCondGasOrOilBoilerNoOAreset | non-condensing gas/oil boiler no outdoor air reset
condGasFurnace | condensing gas furnace
nonCondGasOrOilFurnace | non-condensing gas/oil furnace
ASHPlessThan6TonsDucted | air source heat pump < 6 tons - ducted
ASHPlessThan6TonsNonDucted | air source heat pump < 6 tons - non-ducted
ASHPorVRFgreaterThan6TonsDucted | air source heat pump or VRF >= 6 tons ducted
ASHPorVRFgreaterThan6TonsNonDucted | air source heat pump or VRF >=6 tons non-ducted
electricResistance | electric resistance
PTACorPTHP | packaged terminal air conditioner or heat pump
waterSourceHeatPump | water source heat pump
groundSourceHeatPump | ground source heat pump
air2WaterHeatPump | air to water heat pump
windowAirConditioner | window air conditioner
waterCooledChiller | water cooled chiller
airCooledChiller | air cooled chiller
none | none