## Sheet1
soilType | value | units | Soil thermal conductivity and uninsulated foundation wall R value
k typical | 0.8 | Btu/h-ft-°F | These are fixed values of soil conductivity used for calculating below grade heat loss. The user does not need to enter values here, but they are editable by the user.
k well graded | 1.5 | Btu/h-ft-°F
k dry, fine-grained | 0.5 | Btu/h-ft-°F
k damp, fine-grained | 0.7 | Btu/h-ft-°F
k wet, fine grained | 1 | Btu/h-ft-°F
R typical uninsulated concrete walls | 1.47 | hr-ft2-°F/Btu | This is the R value of a standard uninsulated concrete foundation wall, 8" thick, with the interior air film only,
for use in below grade heat loss calculation. It is sufficiently accurate for thicknesses greater or lesser than 8".