## Sheet1
SpaceType | LPD_WFt2 | EPD_WFt2 | SensGain_BtuHrPerson | LatGain_BtuHrPerson | LgtEFLHday | EquipEFLHday | PeopleEFLHday | Ft2person | Lighting and equipment power densities for each space type, as well as the sensible and latent gains from people.
Residential | 0.9 | 0.5 | 250 | 200 | 3 | 5.8 | 16.55 | 450 | These are standard values used in energy modeling, however the user can and in some cases should edit these values when there is evidence that a particular building is an outlier with regards to power densities and schedules.
Corridor | 1 | 0 | 250 | 200 | 24 | 9 | 0.8 | 3000 | The lighting values should reflect the findings from an on-site energy audit, or from lighting plans.
Stairwell_Elevator | 1.4 | 1.37 | 250 | 200 | 24 | 9 | 0.8 | 3000 | If necessary for best accuracy, the lighting power density for a sample of spaces can be calculated based on the actual fixture
CommonArea | 0.69 | 0.2 | 250 | 200 | 9 | 9 | 7.1 | 200 | wattages and the area of the spaces, where fixture wattages are determined from an audit or from lighting plans.
Mechanical | 1.3 | 1.2 | 250 | 200 | 2.082 | 9 | 0.8 | 10000 | The tables are prepopulated with standard modeling values from sources such as COMNET, RESNET, Energy Star, and LEED, where EFLH have been determined from 24 hour schedules.
Office_Lounge | 0.5 | 0.2 | 250 | 200 | 10.5 | 14.1 | 9.2 | 200 | For multifamily buildings, a very significant input is the lighting EFLH in residential space types, which make up most of the building. The default lighting value of 3 EFLH/day can be adjusted based on information from the site or to calibrate. There is no differentiation between weekdays and weekends or holidays.
Laundry | 1.2 | 0.74 | 250 | 200 | 15.2 | 2.4 | 3.2 | 100
Restroom | 0.9 | 0 | 250 | 200 | 16 | 9 | 0.8 | 33
Fitness | 0.9 | 0.59 | 250 | 200 | 8.6333 | 8.6333 | 0.8 | 1000 | Col. 1. Space Type
Retail | 0.69 | 0.5 | 250 | 200 | 8.6333 | 11.3833 | 5.8333 | 66.6667 | Col. 2. LPD_Wft2. Typical lighting power density in Watts per square foot. LPD for commercial spaces is from ASHRAE standard 90.1-2016.
Restaurant | 1.4 | 1.37 | 250 | 200 | 14.55 | 3.95 | 8.4 | 14.2857 | Col. 3. EPD_Wft2. Typial equipment power density in Watts per square foot, i.e. plug loads. Equipment power density (EPD) is from COMNET.
Theater | 1.2 | 0.74 | 250 | 200 | 11.85 | 11.55 | 6.81 | 10 | Col. 4. SensGain_BtuHrPerson. Typical sensible internal gains from people in Btu per hour per person.
School | 1.2 | 0.69 | 250 | 200 | 14.4 | 13.8 | 8.35 | 40 | Col. 5. LatGain_BtuHrPerson. Typical latent internal gains from people in Btu per hour per person.
Storage | 1.1 | 1.5 | 250 | 200 | 2.082 | 9 | 0.8 | 10000 | Col. 6. LgtEFLHday. Typical lighting equivalent full load hours per day.
Unconditioned | 0 | 0 | 250 | 200 | 0 | 0 | 0 | 10000 | Col. 7. EquipEFLHday. Typical equipment equivalent full load hours per day.
Other | 0 | 0 | 250 | 200 | 0 | 0 | 0 | 10000 | Col. 8. PeopleEFLHday. Typical people equivalent full load hours per day.
Col. 9. Ft2person. Typical occupant density in square feet per person.
Row for unconditioned. If entering space here, enter the lighting and equipment power densities, if any.